## Tabelle1
Parameter | Unit | Category | Initial | Validation_1 | Validation_2 | Validation_3 | Validation_4 | Validation_5 | Validation_6 | Validation_7 | Validation_8 | Validation_9 | Validation_10 | Dataset1 | Dataset1_source
dataset name | str | Information | Initial | Validation_1 | Validation_2 | Validation_3 | Validation_4 | Validation_5 | Validation_6 | Validation_7 | Validation_8 | Validation_9 | Validation_10 | Dataset1
orientation | str | Collector Assembly | song2013 | northsouth | northsouth | northsouth | northsouth | northsouth | northsouth | northsouth | northsouth | northsouth | northsouth | song2013 | SONG, Y. Q., Y. XIANG, Y. B. LIAO, B. ZHANG, L. WU, and H. T. ZHANG. How to decide the alignment of the parabolic trough collector according to the local latitude. 2013 International Conference on Materials for Renewable Energy and Environment (ICMREE 2013). Chengdu, China, 19 - 21 August 2013 ; [proceedings. Piscataway, NJ: IEEE, 2013, pp. 94-97.
a1 | 1/deg | Collector Assembly | 0.000884 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | 8.4924e-05 | -8.7266e-05 | RIFFELMANN, K., T. RICHERT, P. NAVA, and A. SCHWEITZER. Ultimate Trough® – A Significant Step towards Cost-competitive CSP [online]. Energy Procedia. 2014, 49, 1831-1839. Available from: 10.1016/j.egypro.2014.03.194.
a2 | 1/deg^2 | Collector Assembly | 5.369e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | 3.1093e-05 | -3.1071e-05 | RIFFELMANN, K., T. RICHERT, P. NAVA, and A. SCHWEITZER. Ultimate Trough® – A Significant Step towards Cost-competitive CSP [online]. Energy Procedia. 2014, 49, 1831-1839. Available from: 10.1016/j.egypro.2014.03.194.
a3 | 1/deg^3 | Collector Assembly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RIFFELMANN, K., T. RICHERT, P. NAVA, and A. SCHWEITZER. Ultimate Trough® – A Significant Step towards Cost-competitive CSP [online]. Energy Procedia. 2014, 49, 1831-1839. Available from: 10.1016/j.egypro.2014.03.194.
eta_ptr_max | 1 | Collector Assembly | 0.742 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | 0.827 | RIFFELMANN, K., T. RICHERT, P. NAVA, and A. SCHWEITZER. Ultimate Trough® – A Significant Step towards Cost-competitive CSP [online]. Energy Procedia. 2014, 49, 1831-1839. Available from: 10.1016/j.egypro.2014.03.194.
relHeatLosses | 1 | Collector Assembly | 0.06 | [10 empty] | -1
maxWindspeed | m/s | Collector Assembly | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 16 | GÜNTHER, M. JOEMANN, M. CSAMBOR, S. GUIZANI, A. KRÜGER, D. AND HIRSCH, T. Advanced CSP Teaching Materials. Chapter 5 Parabolic Trough Technology, 2011., Page 41
b0 | 1/K | Collector Assembly | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PERNPEITNER, Johannes, Niels LICHTENHÄLER, Philipp ANT, Christoph HAPPICH, and Johannes THOSS. Measurement of Parabolic Trough Receiver Thermal Loss Power and Relative Efficiency under Solar Simulator Light. Test Report, 2012.
b1 | W/(m^2K) | Collector Assembly | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.02421 | 0.044702 | PERNPEITNER, Johannes, Niels LICHTENHÄLER, Philipp ANT, Christoph HAPPICH, and Johannes THOSS. Measurement of Parabolic Trough Receiver Thermal Loss Power and Relative Efficiency under Solar Simulator Light. Test Report, 2012.
b2 | W/(m^2K^2) | Collector Assembly | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | 2.461e-05 | -0.00029279 | PERNPEITNER, Johannes, Niels LICHTENHÄLER, Philipp ANT, Christoph HAPPICH, and Johannes THOSS. Measurement of Parabolic Trough Receiver Thermal Loss Power and Relative Efficiency under Solar Simulator Light. Test Report, 2012.
b3 | W/(m^2K^3) | Collector Assembly | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.556e-07 | 1.2085e-06 | PERNPEITNER, Johannes, Niels LICHTENHÄLER, Philipp ANT, Christoph HAPPICH, and Johannes THOSS. Measurement of Parabolic Trough Receiver Thermal Loss Power and Relative Efficiency under Solar Simulator Light. Test Report, 2012.
b4 | W/(m^2K^4) | Collector Assembly | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | 1.17e-09 | -4.6532e-10 | PERNPEITNER, Johannes, Niels LICHTENHÄLER, Philipp ANT, Christoph HAPPICH, and Johannes THOSS. Measurement of Parabolic Trough Receiver Thermal Loss Power and Relative Efficiency under Solar Simulator Light. Test Report, 2012.
A_aperture_sf | m^2 | Collector Field | 909060 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800 | 1372800
SF_density | 1 | Collector Field | 0.383 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.3051 | 0.434
ratedFieldOutputHeat_W | W | Collector Field | 674522520 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1
eta_cleaness | 1 | Collector Field | 1 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.96 | BELLMANN, Philipp, Fabian WOLFERTSTETTER, Ricardo CONCEIÇÃO, and Hugo G. SILVA. Comparative modeling of optical soiling losses for CSP and PV energy systems [online]. Solar Energy. 2020, 197, 229-237. Available from: 10.1016/j.solener.2019.12.045.
add_losses_coefficient | W/m^2K | Collector Field | 0 | 0 | 0 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | 0.108 | JÜRGEN DERSCH, and SIMON DIECKMANN. Greenius Help & Manual. 2018.
efficencyDropPerYear | 1 | Collector Field | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Assumed
I_DNI_nom | W/m^2 | Parasitic losses | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 900 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
PL_plant_fix | 1 | Parasitic losses | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | 0.0055 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
PL_sf_track | 1 | Parasitic losses | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.0026 | 0.016 | 0.016 | 0.016 | 0.0026 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
PL_sf_pumping | 1 | Parasitic losses | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.003 | 0.0115 | 0.0115 | 0.05 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
PL_plant_pumping | 1 | Parasitic losses | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
PL_plant_other | 1 | Parasitic losses | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | 0.019 | GAFUROV, Tokhir, Julio USAOLA, and Milan PRODANOVIC. Modelling of concentrating solar power plant for power system reliability studies [online]. IET Renewable Power Generation. 2015, 9(2), 120-130. Available from: 10.1049/iet-rpg.2013.0377.
relTMplant | J/K | Plant | 1100 | 1100 | 1100 | 1100 | 3688 | 3688 | 1100 | 3688 | 3688 | 3688 | 3688 | 3688 | Calibrated with values from: JÜRGEN DERSCH, and SIMON DIECKMANN. Greenius Help & Manual. 2018.
maxHTFTemperature | °C | HTF | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 385 | 550 | 560 - 10 security margin from:BENOIT, H., L. SPREAFICO, D. GAUTHIER, and G. FLAMANT. Review of heat transfer fluids in tube-receivers used in concentrating solar thermal systems: Properties and heat transfer coefficients [online]. Renewable and Sustainable Energy Reviews. 2016, 55, 298-315. Available from: 10.1016/j.rser.2015.10.059.
minHTFTemperature | °C | HTF | 15 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 260 | 240 + 20 security margin from:BENOIT, H., L. SPREAFICO, D. GAUTHIER, and G. FLAMANT. Review of heat transfer fluids in tube-receivers used in concentrating solar thermal systems: Properties and heat transfer coefficients [online]. Renewable and Sustainable Energy Reviews. 2016, 55, 298-315. Available from: 10.1016/j.rser.2015.10.059.
inletHTFTemperature | °C | HTF | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | Assumed / fits with most plants in: SOLARPACES. CSP Projects Around the World [online] [viewed 10 June 2021]. Available from: https://www.solarpaces.org/csp-technologies/csp-projects-around-the-world/.
lifetime | a | genral | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
discretizationmethod | str | Simulation Method | euler explicit | euler explicit | euler explicit | euler explicit | euler explicit | euler implicit | euler implicit | euler explicit | euler explicit | euler explicit | euler explicit | euler explicit
Collector Assembly | str | Information | Gafurov, Greenius | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014 | Ultimate Trough_2014
HTF | str | Information | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Therminol VP-1 | Solar Salt
Sources | str | Information | Gafurov, losses from Greenius | [6 empty] | PL from Gafurov
Comment